FIELD DIELECTRIC TESTING RECORD

CX: 		MODEL: 		S/N’s:

TEST ITEM DESCRIPTION: 		                                                                 P/N:

TEST CONDITIONS – Refer to FIELD DIELECTRIC TESTING WORK INSTRUCTION #11180.

All equipment is tested for 60 secs (min) to 65 secs (max) duration at 1000V plus 2 times the highest rated voltage.  NOTE: Exceeding the Test Voltage or Test Duration can damage wiring and equipment.

| Example Rated Voltages | Example Test Voltage |
| --- | --- |
| 120V | 1240V (min) to 1300V (max) |
| 208V | 1416V (min) to 1450V (max) |
| 380V | 1760V (min) to 1800V (max) |
| 480V | 1960V (min) to 2000V (max) |

Identify any components that were isolated from the test (to prevent component damage):

DIELECTRIC TEST – Refer to FIELD DIELECTRIC TESTING WORK INSTRUCTION #11180.

|  | Rated Voltage | Test Voltage | Test Duration | Test Results Acceptable? |  |
| --- | --- | --- | --- | --- | --- |
| ACTUAL | V | V | secs | YES | NO |

Dielectric Test Instrument Model:                                      S/N:

Calibration Expiry Date:

MM / DD / YYYY

Our job is not done until our clients are growing confidently. We deliver on Conviron’s commitments by installing and commissioning controlled environment equipment on-specification, on-time, and on-budget.

Please return a copy of this completed form to the Installations Department.

Completed By: 		Date:  						   	   	   MM   /   DD   /    YYYY